Seismic risk of sliding ground-mounted rigid equipment

Miguel A Jaimes,a) and Gabriel Candiab)

ABSTRACT

This study discusses a general formulation for risk assessment of ground-mounted rigid sliding equipment and contents during earthquakes. The displacement and acceleration response of blocks during earthquakes and risk were examined for four types of support conditions: (1) equipment simply supported on a foundation; (2) equipment restrained to a fixed base; (3) equipment supported on a linear viscoelastic isolation system; and (4) equipment supported on a single concave spherical sliding (SCSS) isolation system. Because empirical fragility functions for sliding-dominated equipment remain insufficient, the present study relies on numerical analysis and a solid physical background to compute risk. These results should aid designers in the selection of appropriate support conditions or mitigation measures for rigid equipment and contents in seismic-prone regions.

As an example, the seismic response of rigid equipment is illustrated using ground motions from the recent (2017) Mexico earthquakes, which damaged several pieces of equipment in the largest oil refinery in Mexico. Furthermore, the effects of site-to-source distance for sites located on ﬁrm soil are studied in detail, as the frequency content of these ground motions differ signiﬁcantly and play a key role in the reliability of sliding blocks. The results of the seismic risk assessment show that low-frequency ground motions (i.e., far-field site) generally yield lower maximum and residual equipment displacements compared to those from high-frequency ground motions (i.e., near-source site). This investigation also concludes that the reliability of freestanding and base-isolated equipment in terms of maximum absolute block accelerations is higher than that of anchored equipment.

Keywords sliding blocks; seismic isolation; spherical sliding bearings; seismic risk; maximum block acceleration; maximum block displacement

# Introduction

Freestanding equipment at critical facilities are highly vulnerable to rocking, overturning and residual lateral displacement during earthquakes (e.g., Soong et al. 2000; Lopez Garcia and Soong 2003a,b; Alhan and Gavin 2005; Hutchinson and Chaudhuri 2006; Jaimes et al. 2013; Lin et al. 2015; Jaimes and Candia 2018). To improve the response of the equipment, mitigation measures such as restrainers or base-isolated slabs have been developed, but even these solutions may result in excessive damage due to large ground accelerations (Lopez Garcia and Soong, 2003b). In non-slender blocks, one way to prevent rocking is to allow the block to slide freely. However, it is necessary to quantify and limit the amount of slip to avoid the impacts against adjacent objects or building components, as well as large accelerations, to minimize the internal damage of sensitive equipment.

On September 7, 2017, a Mw 8.2 intermediate-depth normal earthquake struck the Gulf of Tehuantepec in Chiapas, Oaxaca (Mexico), being the largest earthquake in the region since the 1932 Mw 8.2 Jalisco earthquake. The 2017 Oaxaca earthquake severely damaged houses, heritage buildings, bridges, and power stations located near the epicenter. No structural damage was reported at the state-owned Salina Cruz Refinery, the largest oil refinery in Mexico with an installed capacity of 330,000 barrels per day. The earthquake, however, induced large lateral displacements on the electricity generators (Figure 1) that power the plant (PEMEX 2017). These generators affected an adjacent steam turbine and auxiliary equipment, causing severe damage to its internal components. As a result, the plant was shut down as a precaution, and operations resumed 2.5 months later with the aid of two leased diesel generators; unfortunately, a leased generator was damaged during the transportation and installation. Further details are presented in Section 3.

The sliding response of freestanding rigid blocks to a base excitation is founded on the principles of rigid body dynamics, for which a vast body of literature exists (e.g., Newmark 1965; Lopez Garcia and Soong 2003a,b). After studying the seismic behavior of earth dams and embankments, Newmark 1965 developed a simplified method to estimate residual displacements of a rigid soil block sliding on a rough surface. In this method, residual displacements are computed as the double integral of the acceleration in excess of the yield acceleration, i.e., the acceleration level required to initiate slip in the system. This pioneering work became a standard for evaluating earth slopes and embankments.

Figure 1. Damage by excessive lateral displacement of an electricity generator at the Salina Cruz Refinery during the 2017 Mw 8.2 Oaxaca, Mexico earthquake. a) Electricity generator TG-2 (turbine, generator and auxiliary equipment), and b) damage of floor slab due to collision between the floor slabs.

Aslan et al. (1975) conducted shaking table tests to study the sliding response of rigid concrete blocks under horizontal and vertical excitations and developed analytical predictions of the block response within a 10% error. Jones and Shenton (1990) used numerical analysis to study the sliding-rocking response of rigid blocks to earthquake ground motions for a range of contact parameters. Shenton and Jones (1991a,b) described the governing differential equations of motion for freestanding rigid bodies, and Agbabian et al. (1991) discussed analytical and experimental techniques for evaluating earthquake rocking, overturning, and sliding susceptibility of museum objects. Several authors (e.g., Shenton 1996; Pich 1995; Shao and Tung 1999; Taniguchi 2002; Aydin 2006) have derived the equations of motion and the initiation criteria of the different response modes of freestanding rigid blocks, including sliding, rocking, uplift, and sliding-rocking modes. Shao and Tung (1999) also estimated the sliding distance and the probability of overturning for nonsymmetrical rigid bodies considering a suite of 75 real earthquake recordings. More recently, Choi and Tung (2002) showed that Newmark’s model could effectively reproduce the earthquake-induced displacement of rigid blocks standing at ground level or at the different floors of a building if appropriate adjustment factors are used.

Lopez Garcia and Soong (2003a) studied the seismic fragility of unrestrained block-type equipment considering two failure modes: excessive relative displacement and excessive absolute acceleration. Hutchinson and Chaudhuri (2006) developed analytical fragility functions for unrestrained scientific equipment subjected to ground motions, and Konstantinidis and Nikfar (2015) conducted experiments to study the sliding response of freestanding and anchored laboratory equipment in base-isolated buildings. More recently, Lin et al. (2015) studied the sliding of contents in simple linear-elastic structures subjected to base accelerations.

Seismic mitigation measures against block sliding (e.g., base isolation or restrainers) have been studied numerically and experimentally. When properly designed, the base isolation of rigid blocks can effectively reduce sliding and the accelerations transmitted to the block (e.g., Alhan and Gavin 2005). However, conventional passive isolation systems may suffer from low-frequency resonance, especially when subjected to long-period pulses such as the ground motions from near-fault earthquakes (Makris and Chang 2000). This effect leads to large shaking amplification of the isolation floor, compromising the isolated object (Makris and Chang 2000, Alhan and Gavin 2005, Contento and Di Egidio 2014).

Lopez Garcia and Soong (2003b) studied restrained blocks under earthquake loading; the authors showed that restrainers (e.g., cables and anchors) reduce the block’s sliding response at the expense of increased accelerations, which can be harmful to precision equipment. Configuration details of base-isolated and restrained equipment are discussed in the next section.

The purpose of the present study is to evaluate the seismic risk of sliding rigid blocks, such as power generators, based on numerical solutions of the governing differential equations and the site-specific seismic hazard. Four types of support conditions are considered in the analysis: (1) equipment freestanding on the foundation; (2) equipment restrained to a fixed base; (3) equipment supported on a linear viscoelastic isolation system; and (4) equipment supported on a single concave spherical sliding (SCSS) isolation system. As an example, this study uses Mexican seismicity and Mexican electrical equipment to illustrate the effect of near-source and far-ﬁeld ground motions on the seismic risk. Design recommendations are provided for the type of sliding mitigation measure appropriate for these different seismic environments. Finally, this study provides reference values of the seismic risk for typical sliding equipment subject to ground motions with different frequency content (i.e., near-source versus far-ﬁeld ground motions). Additionally, this study uses records from the 2017 Mw 8.2 Oaxaca earthquake (Mexico), which damaged several equipment located near the rupture area.

# METHODOLOGY

The seismic risk of sliding rigid blocks is described in three steps: (1) evaluation of the seismic response; (2) development of sliding and acceleration fragility functions; and (3) convolution of seismic hazard and fragility functions. These steps are explained next.

2.1 SEISMIC RESPONSE

Four equipment configurations are considered in this study: (1) equipment simply supported on a foundation; (2) equipment restrained to a fixed base; (3) equipment supported on a linear viscoelastic isolation system; and (4) equipment supported on a single concave spherical sliding (SCSS) isolation system. In all cases, the base excitation acts along the horizontal axis. In addition, the dimensions of the equipment are such that rocking and uplifting motions cannot occur. Thus, the position of the block relative to the foundation is described with a single degree of freedom x, as shown in Figure 2. The governing equations of motion for each configuration are presented herein.

Figure 2. Schematic view of rigid electrical equipment in sliding motion: a) equipment simply supported on a fixed base; (b) equipment restrained to a fixed base; c) equipment supported on a seismic base isolator on linear viscoelastic bearings; and d) equipment supported on a SCSS isolator.

## 2.1.1 Equipment simply supported on a fixed base

The relative position of a simply supported block due to ground acceleration xg (Shenton and Jones 1991a; Shenton 1996; Lopez Garcia and Soong 2003a) is described as the second-order differential equation

| mx+μksgnxmg=-mxg | (1) |
| --- | --- |

where x is the block acceleration relative to the ground, x is the relative block velocity, the term μksgnxmg is the friction force developed at the interface, μk is the coefficient of kinetic friction, and g is the gravity acceleration. Dividing both sides of Equation (1) by the block mass m, the equation of motion reduces to

| x=-μksgnxg-xg | (2) |
| --- | --- |

Note that the friction force always acts in the direction opposite to the velocity, and when the inertia forces are not sufficient to mobilize the friction, no slip occurs, in which case the equation of motion is x=0.

## 2.1.2 Equipment simply supported on a linear viscoelastic isolation system

The equation of motion for a block simply supported on a linear viscoelastic isolation system can be derived from Equation (1) by substituting xg with xg+xb, where xb is the position of the isolated base relative to the ground. Then, Equation (1) becomes

| mx+μk∙sgnxmg=-mxg+xb | (3) |
| --- | --- |

Moreover, the horizontal force equilibrium of the isolated base gives

| -kbxb-cbxb=mbxg+xb+mxg+xb+x | (4) |
| --- | --- |

where mb is the mass of the isolated base, and kb and cb are the stiffness and damping of the isolation system, respectively. In Equations (3) and (4), the acceleration terms xb and x can be written explicitly as a function of the state variables xb, xb, x, and x as

| xb=-γx-2ξbωbxb-ωb2xb-xg | (5.1) |
| --- | --- |
| x=-xg+xb-μk∙sgnxg | (5.2) |

where γ=mmb+m, ωb=kbmb+m and ξb=cb2ωbmb+m.

## 2.1.3 Equipment supported on a bilinear isolation system

Analogous to Equation (4), the equation of motion for a block sliding on a bilinear isolated base of strength Q and yield displacement uy can be written as

| -kbx-Q∙z=mbxg+xb+mxg+xb+x | (6) |
| --- | --- |

where kb represents the second slope of the bilinear idealization, mb is the mass of the isolated base, and z is a dimensionless Bouc-Wen parameter (Equation 7) to characterize the forces in the isolator.

| zt=1uyxb-ζxb⋅z⋅zn-1-βxbzn | (7) |
| --- | --- |

This formulation reasonably approximates the response to two types of base-isolation systems: single concave spherical sliding (SCSS) bearings, in which case the strength Q takes the form Q=μbm+mbg, where μb is the friction coefficient, and lead rubber bearings with horizontal strength Q. Combining Equations (3), (6) and (7), the acceleration terms xb and x can be written as

| xb=-γx-Qm+mb z-ωb2xb-xg | (8.1) |
| --- | --- |
| x=-xb+xg-μk∙sgnxg | (8.2) |

In the illustrative examples, a very small value for the yield displacement was adopted for the base isolation (uy=0.25 mm, Mokha et al. 1988), which approximates the ‘stick-slip’ behavior of sliding systems. Vassiliou and Makris (2012) showed that the response of the system is not very sensitive to small variations in uy.

A key element influencing the displacement response of free and isolated blocks is the coefficient of kinetic friction. Figure 3 shows the response in terms of residual displacements (top axes) and maximum displacements (bottom axes) of a freestanding and linear viscoelastic base-isolated block subjected to a symmetric Ricker or ‘Mexican Hat’ wavelet (Vassiliou and Makris, 2012) of predominant period Tp=1 s, amplitude 0.1g≤ap≤2g, and kinetic friction 0.05≤μk≤0.4. The dark line in each plot in Figure 3 marks the transition between the ‘friction efficient zone’ and the ‘friction inefficient zone’. In the friction efficient zone, an increase in kinetic friction decreases both the residual and maximum displacements, whereas the opposite is observed above the transition line. Additionally, notice that an increase in the acceleration amplitude always leads to increasing displacements. Finally, the results from this example show that the displacements in the linear-elastic base-isolated block relative to its base are larger than the displacements in the simply supported block.

Figure 3. Contours of residual and maximum displacements (in meters) for (a) a freestanding block and (b) a linear viscoelastic base-isolated block (Tb=2.0 s, γ=0.1, ξb=0.25) subjected to a symmetric wavelet of period Tp=1 s.

## 2.1.2 Equipment restrained to a fixed base

Lopez Garcia and Soong (2003b) developed the equation of motion for equipment anchored to a base with four linear-elastic prestressed rods and a small displacement formulation. Herein, we extended this formulation to account for large displacements and prestressed elasto-plastic-brittle (PEPB) anchors with ultimate strength Fu, yield deformation vy, and ductility capacity ratio μ. For simplicity, the stiffness of the elastic branch K is defined in terms of the natural period Teq of a block restrained with four linear elastic anchors as defined in Lopez Garcia and Soong (2003b). Thus, the element stiffness is simply K=π2mTeq2L0x02, where L0 is the anchor length and x0 is the anchor offset along the x direction, as shown in Figure 2b. The governing equation for the anchored equipment is

| x=-xg-μk⋅sgnxg+1mFY-1mFX | (9) |
| --- | --- |

where the term FX is the sum of the left and right anchor loads projected in the horizontal direction and the term FY is the sum of the left and right anchor loads projected in the vertical direction. Both terms account for the prestress load T0 and the effect of geometric nonlinearity. For a complete derivation of the terms FX and FY, refer to appendix A.

A schematic representation of the load-deformation relation of a PEPB anchor is shown in Figure 4a. Fracture in the anchor occurs if the element deformation v satisfies v-v0>vu, where v0=-T0/K is the initial deformation due to prestress, and vu=μ vy is the ultimate deformation. Once the anchor breaks, the anchor load is zero.

Figure 4. (a) Schematic representation of a stress-strain relationship of a PEPB element and (b) flowchart for the calculation of the anchor load f and fracture index I in discrete form.

To incorporate the hysteretic behavior of the PEPB element into the numerical integration scheme of Equation (9), two memory parameters are defined, namely, the anchor load f and the fracture index I, such that I=0 before the anchor breaks and I=1 after the anchor breaks. A discrete-time representation of the load-deformation relationship of the PEPB element is presented in Figure 4b, where vk, fk and Ik represent the deformation, load, and fracture index, respectively, of the anchor at time tk, and vk+1, fk+1 and Ik+1 are the deformation, load, and fracture index, respectively, of the anchor at time tk+1.

Importantly, since actual anchored equipment have natural period 0.05 s<Teq<0.2 s (Lopez Garcia and Soong 2003b), a value of Teq=0.1 s is considered in this study. The key factors that influence the response of the restrained blocks are the strength and ductility of the anchors. For example, consider a restrained block subjected to a symmetric Ricker wavelet with an acceleration amplitude of 1g and a predominant period of 1 s. For a fixed value of kinetic friction μk=0.1, natural period Teq=0.1 s, anchors with strength ratio 0.0≤Fu/W≤0.6, and ductility ratio 1≤μ≤3, the response of the block is shown in Figure 5 in terms of maximum displacement (D) and maximum block acceleration (A). In both diagrams, the region to the left of the dashed line corresponds to Fu/W and μ combinations resulting in the fracture of both anchors, and vice versa. Notice from Figure 5a that D is significantly amplified for a wide range of Fu/W values, but D decreases for Fu/W>0.4 and approaches ‘zero’ for Fu/W~0.6. This improved displacement control contrasts with the increasing maximum block acceleration, as shown in Figure 5b. From this figure, it is apparent that A is not very sensitive to variations in the ductility ratio above ~1.5-1.6, but it increases monotonically with the anchor strength. Although the diagrams in Figure 5 correspond to a simple wavelet, they can be reproduced for any input ground motion, thus aiding designers in the selection of appropriate anchor parameters. Finally, notice from Equations (1) to (9) that the block response is not an explicit function of the block dimensions, as it only depends on its support conditions.

## 2.1.4 Numerical integration and stopping criterion

Equations (2), (5), (8) and (9) were written in state format and integrated numerically using an explicit 4th order Runge Kutta method (Butcher 2016). Integration was carried over the entire length of the ground motion.

Figure 5. Contours of (a) maximum block displacements, D (in meters), and (b) maximum block acceleration, A (in g’s) as a function of the strength Fu/W and ductility ratio μ of the anchor. Simulations leading to rupture of both anchors are plotted to the left of the dashed line.

## 2.1.5 Validation examples

To verify the fidelity of the solution to Equation (1), an example available in the literature was reproduced herein. The response of a simply supported block to the ground motion Takatori-000 from the 1995 Kobe earthquake, Japan, successfully matched the results of Konstantinidis and Nikfar (2015), as shown in Figure 6a (compare to Figure 3 in Konstantinidis and Nikfar 2015). For the case of blocks restrained to the base with elastoplastic anchors and large horizontal deformations, no benchmark solutions were found in the literature. Nevertheless, as shown in Figure 6b, our solution of Equation (9) successfully reproduced the response of a block with linear elastic anchors (i.e., very large ratio Fu/W) obtained using the small-displacement approximation by Lopez Garcia and Soong (2003b) (refer to Equation 28 in Lopez Garcia and Soong 2003b). In this example, notice that the block displacements satisfy x≪x0.

## 2.2 FRAGILITY FUNCTIONS

Fragility functions for a given engineering demand parameter (EDP) are defined as the probability of exceeding a demand level conditioned on the occurrence of a ground motion intensity (IM), i.e., P(EDP>z|IM) vs IM. In this study, the structural reliability of sliding blocks is assessed independently for two EDPs: the maximum block displacement relative to its base (i.e., D=maxx) and the maximum absolute acceleration (i.e., A=maxx+xg or A=maxx+xb+xg). To develop the fragility functions, an incremental dynamic analysis (IDA, Vamvatsikos and Cornell 2002) was implemented. For this purpose, the equipment was subjected to a suite of horizontal ground motions scaled to identical peak ground acceleration (PGA) values. Then, for each ground motion level, the probability that an EDP exceeds a test value z is computed as the number of simulations where EDP>z divided by the total number of simulations.

(b)

(b)

(a)

(a)

Figure 6. (a) Response of a sliding rigid block (μk=0.1) subjected to the ground motion Takatori-000 from the 1995 Kobe earthquake (NGAwest2 RSN1120, component H1) and (b) response of a block with linear elastic anchors (μk=0.05, Teq=0.7 s, x0=0.5m, y0=0, z0=0.5m) computed using the small-displacement formulation by Lopez Garcia and Soong (2003b) and the current large-displacement approach.

## 2.2.1 Maximum block displacement

Engineering judgment is required to select the acceptable performance for each piece of equipment. The probability of failure of sliding-dominated equipment was obtained for displacement values between 0.01 and 1.5 m, which range from negligible displacements up to large displacements that could lead to impacts against nearby objects and severely damage the equipment’s internal components or displacements in excess of the support margins. To distinguish between zero and nonzero block displacements (d), the probability density function (pdf) of d conditioned on the ground shaking intensity y can be written as

| fDd¦ y=δd-d0p+1-pfD(d) | (10) |
| --- | --- |

where δ∙ is the Dirac delta function, d0=0.01m is the displacement threshold of the equipment regarded as negligible or ‘zero’, p is the probability mass at D=d0, which lumps all the displacement values D≤d0, and fD(d) is the pdf for D>d0. This approach is similar to that used by Travasarou and Bray (2007) for the treatment of residual slope displacements computed from a stick-slip model. Nevertheless, if deemed necessary, other displacement thresholds can be adopted within the proposed methodology. From Equation (10), the probability of exceeding a displacement level d, i.e., PD>d|y, can be easily obtained.

## 2.2.2 Maximum absolute block acceleration

For simply supported blocks on a fixed base, the maximum absolute block acceleration is A=maxx+xg. Based on Equation (2), the probability that A exceeds a test value a is therefore

| PA>aPGA= HPGA-a if PGA≤μkg Hμkg-a otherwise | (11) |
| --- | --- |

where H(⋅) is the Heaviside function. Equation (11) is also valid for equipment simply supported on an isolated base, except that the maximum block acceleration is A=maxx+xg+xb. For anchored equipment, the anchors transmit accelerations to the block in excess of μkg and Equation (12) should be used instead. Since no analytical solution exists for A when PGA>μkg+1mFY, the fragility function in this case must be evaluated numerically from IDAs.

| PA>aPGA= HPGA-a if PGA≤μkg+1mFY NA>aNt otherwise | (12) |
| --- | --- |

In Equation (12), NA>a is the number of simulations in which A>a, and Nt is the total number of simulations. Computing PA>aPGA according to Equation (11) or (12) is immediate, and it can be achieved without resorting to analytical fragility functions. All fragility functions presented herein use PGA as the ground motion intensity measure (IM) because hazard analyses for PGA are widely available in engineering practice and easier to communicate to decision makers. Nevertheless, the same scheme is applicable to other IMs used to predict sliding of rigid blocks (e.g., Hutchinson and Chaudhuri 2006, Gelagoti et al. 2012).

## 2.3 EVALUATION OF SEISMIC RISK

The rate of exceedance of the maximum block displacements λDd can be obtained as the convolution of the displacement fragility function PD>d  y) and the site-specific seismic hazard curve λyy as

| λDd=-yPD>d y)dλy(y)dydy | (13) |
| --- | --- |

A similar approach is used to compute the rate of exceedance of the maximum block acceleration λAa; for simply supported equipment on a fixed base or an isolated base, a close inspection of Equations (11) and (13) leads to

| λAa=λya if a≤μkg 0 otherwise | (14) |
| --- | --- |

The first part of this equation (a≤μkg) corresponds to a no-slip condition, whereas in the second part, slippage takes place. Importantly, for anchored equipment, the λA values for a>μkg are nonzero and must be evaluated numerically from IDAs.

3. AN ILLUSTRATIVE EXAMPLE

3.1 EQUIPMENT STUDIED

The present example evaluates the earthquake sliding risk of equipment typically used in Mexican refineries (see Figure 1). The analysis considers a nonslender rectangular block with mass m≈ 8.7 kN·s2/m and three values for the coefficient of kinetic friction: μk=0.10, 0.15, and 0.20.

Anchored blocks were modeled using four PEPB elements with lengths x0=0.5 m, y0=0, and z0=0.5 m; natural period Teq=0.1s (i.e., K=17,173 kN); and ductility ratio μ=2.0. A parametric analysis considered anchor strength ratios Fu/W= 0.2, 0.3 and 0.4 with no prestress load. This combination of anchor stiffness and strengths corresponds to yield deformations of vy=1.0, 1.5 and 2.0 mm. In addition, setting the anchor strength at Fu/W=0.2, the influence of the prestress load was studied for ratios T0/W= 0.05, 0.10, and 0.15 (i.e., equivalent to 25%, 50%, and 75% of Fu).

For the linear viscoelastic and SCSS base-isolated systems, the analyses were conducted for a mass ratio γ=mmb+m=0.1. The lateral stiffness of the isolation system kb=4π2(mb+m)/Tb2 was computed assuming natural periods of Tb=1.0, and 2.0 s. In the case of a bilinear isolation system, the sliding friction coefficient ξb=0.25 and yield displacement uy=0.25 mm were set after Vassiliou and Makris (2012), and the Bouc-Wen parameters ζ=β=n=1 were used after Jaimes and Candia (2018).

3.2 SEISMIC HAZARD AND GROUND MOTION SELECTION

## 3.2.1 Seismic Hazard

To evaluate the influence of near-source and far-field ground motions, sliding risk analysis was conducted for equipment hypothetically placed at or near the ground motion stations SCRU (near-source, Site 1) and CU (far-field, Site 2). Station SCRU (16.187°N, 95.209°W) is located on a rock outcrop at the Oaxaca subduction zone, just 120 km northwest of the epicenter of the great Mw 8.2 Chiapas earthquake of 2017. Analogously, station CU is located in Mexico City (19.330°N, 99.181°W) over thick deposits of basaltic lava flows at a distance of ~300 km west of the Michoacán subduction zone and 110 km northwest of the Mw 7.1 2017 Puebla earthquake. Both stations are located on class B sites according to ASCE/SEI 7-10 (2010).

The rate of exceedance of PGA at each location was computed through a standard probabilistic seismic hazard analysis (PSHA). Three seismic source types were considered along the Pacific coast of Mexico, as shown in Figure 7 (Ordaz and Reyes 1999; Jaimes and Reinoso 2006), each with specific ground motion models (GMMs). The ground motion models used within each source type are summarized in Table 1; for additional details of the seismic hazard model used, refer to Jaimes and Candia (2018).

Table 1 – Ground motion models (GMMs) used in the seismic hazard computation

| Source type | SRCU sites (near-source) | CU sites (far-field) |
| --- | --- | --- |
| Interface | Arroyo et al. (2010) | Jaimes et al. (2006) |
| Intermediate depth (slab) | Garcia et al. (2005) | Jaimes et al. (2015) |
| Shallow crustal | Abrahamson and Silva (1997) | Jaimes et al. (2016) |

The seismic hazard was implemented in the software SeismicHazard (Candia et al. 2019), and the results are shown in Figure 8 in terms of the mean annual rate of exceedance of PGA, λy.

Figure 7. Mexican seismic sources after (Ordaz and Reyes 1999, Jaimes and Reinoso 2006).

Figure 8. Annual rate of exceedance of PGA at site 1 (near-source) and site 2 (far-field).

## 3.2.2 Ground motions

The dynamic response of sliding equipment is highly sensitive to PGA, peak ground velocity (PGV), and frequency content, among other IMs. To capture the influence of the frequency content of the ground motion on the sliding response, this study uses different criteria to obtain either near-source or far-field ground motions.

In the first case (i.e., near-source ground motions), a dataset of 12 Mexican earthquakes (6 ≤ Mw ≤ 8.2) containing 32 near-source ground motions was selected (Table 1A). The near-source ground motions have an average period Tave (Rathje et al. 1998) between 0.02 s and 0.56 s (i.e., high frequency content), as shown in Figure 9. Watson-Lamprey & Abrahamson (2005) showed that scaling factors as high as 20 introduce no bias in the median response of rigid sliding blocks. Herein, the 32 selected ground motions required maximum linear scaling factors (SFs) of 10 to cover the range of intensities needed to develop the fragility functions and the hazard levels of interest.

Figure 9. Average period of input ground motions considered for risk analysis

A summary of the earthquake parameters is shown in Table B1 in Appendix B; the location of the epicenters and the ground motion stations is presented in Figure 10.

In the second case (i.e., far-field ground motions), we adopted a set of 48 synthetic ground motions computed in accordance with the 2017 Mexico City Seismic Design Provisions (NTCD-2017; 24 ground motions due to intermediate depth intraslab mechanism and the remaining due to subduction mechanism). The seed ground motions were obtained from the September 19, 2017, Mw 7.1 intermediate depth instraslab earthquake, and the September 19, 1985, Mw 8.1 subduction interface earthquake, both recorded at station CU. These ground motions preserve the main characteristics of the seed records; for instance, the average period of the synthetic ground motions are scattered between 0.13 s and 2.2 s, which is the typical distribution of the average period observed in actual CU records.

Figure 10. Epicenters of selected earthquakes and location of ground motion stations.

The reason for using synthetic - and not actual - ground motions is the limited number of events recorded at station CU that result in scaling factors less than 10 (only four records from events 1 and 12 in Table B1). These design provisions incorporate the use of an intensity-based assessment approach (i.e., spectra matching, Kiureghian and Neuenhofer 1992) to undertake rigorous nonlinear analysis of structural systems and a site-specific uniform hazard spectra (UHS) for the generation and scaling of ground motions. Since the ground motions must collectively represent the design earthquakes, it is required that the source mechanism of the seed records be representative of the local seismicity and that their frequency and energy content be compatible with those observed in real records. Based on seismic hazard deaggregation studies, the recent design provisions establish that the design earthquakes within Mexico City must be mainly controlled by two seismic scenarios (NTCD-2017): (1) an intermediate depth instraslab event with a magnitude Mw=7.5 at a rupture distance of 150 km and (2) a subduction event with magnitude Mw=7.8 at a distance of 265 km. In this regard, linear scaling factors less than 10 were used to cover the range of intensities needed to develop the fragility functions. Research is underway to assess the consequences of linearly scaling ground motions within the context of an incremental dynamic analysis of sliding rigid bodies.

## 3.3 Seismic RESPONSE OF ELECTRICAL EQUIPMENT

For each support condition (freestanding, anchored, or base isolated), the response of the equipment due to the 32 near-source and 48 far-ﬁeld ground motions was computed numerically. Ground motions were scaled to PGA between 0.05 and 1.2g (near-source), in 0.05g increments and between 0.05 and 0.35g (far-ﬁeld), in 0.02g increments, from which fragility functions were developed. The next examples discuss the sliding response of three identical blocks with different support conditions: simply supported, linear viscoelastic base-isolated (γ=0.1, Tb=2π/ωb=2.5 s, and ξb=0.25), and anchored to a fixed base (Teq=0.1 s, Fu/W=0.3, T0=0, μ=2). For the three blocks, a friction coefficient of μk=0.1 was considered at the support.

In the first example, consider three blocks subjected to the east-west component of the ground motion recorded at station SCRU during the Mw 8.2 Chiapas earthquake of 2017. A factor of 4.3 was used to scale PGA to 1.0g. The ground acceleration and the block response histories are presented in Figure 11. This plot shows that in the simply supported equipment (left) and the linear viscoelastic base-isolated equipment (middle), the maximum block acceleration is A=μkg=0.1 g, i.e., the mobilization of the shear strength at the support prevents the block from developing larger acceleration values. In contrast, the anchored equipment (right) develops large accelerations in the early phase of the ground motion, as the restrainers transmit acceleration pulses to the equipment in excess of μkg. After the anchor’s fracture (t≈24 s), the block behaves as a freestanding block, and the maximum accelerations remain bounded by μkg. On the other hand, the maximum displacement D is nearly identical for the simply supported and anchored equipment (D ~0.25 m) and slightly lower in the linear viscoelastic base-isolated equipment (D ~0.23 m). Finally, note that the residual displacement in the simply supported anchored blocks is approximately 0.09 m, almost twice that computed in the linear viscoelastic base-isolated block (0.046 cm). This level of permanent displacement during strong ground shaking may render equipment unusable or significantly damaged.

In the second example, the same three blocks were subjected to the east-west component of the ground motion recorded at station CU (far-ﬁeld) during the 2017 Puebla earthquake. A scale factor of 6.2 was applied to yield a PGA of 0.35g; results from these analyses are shown in Figure 12. Similar to example 1, the maximum block acceleration is bounded by μkg in the simply supported blocks. In contrast, the anchors did not fail, and the anchored block developed a maximum acceleration of A≈0.58g. In terms of maximum displacements D, the freestanding block reached 5.4 cm, whereas the base-isolated block and the anchored block developed D values close to zero. The permanent displacement in the three support conditions studied was less than 1 cm. Despite the large ground motion intensity, the benefits of displacement mitigation measures are not evident from this example. A proper assessment of these demand parameters is critical for retrofitting and designing sensitive equipment because they provide the basis for risk-based decision making.

Figure 11. Seismic response of equipment to the September 7, 2017, Mw 8.2 earthquake recorded at the SCRU station (near source) scaled to PGA=1.0g. Left: equipment simply supported on a fixed base; middle: equipment supported on a linear viscoelastic isolation system; and right: equipment anchored to a fixed base.

Figure 12. Seismic response of equipment to the September 19, 2017, Mw 7.1 earthquake recorded at the CU station (far-ﬁeld) scaled to PGA=0.35g. Left: equipment simply supported on a fixed base; middle: equipment supported on a linear viscoelastic isolation system; and right: equipment restrained to a fixed base.

## 3.4 FRAGILITY FUNCTIONS

After running the IDAs, the fragility functions for the maximum block displacement D and the maximum block acceleration A are computed for each block configuration as described in Section 2.2.

To illustrate the effects of the ground motion variability on the displacement D, the next example shows a cross section of the fragility function P(D>d|PGA) for fixed values of the ground shaking intensities: y=0.3, 0.5 and 1g (near source, left) and y=0.15, 0.25 and 0.35g (far-field, right), and displacement values up to 2 m. The results in Figure 13 consider equipment with four support conditions on the foundation: a) freestanding, b) anchored (Teq=0.1 s, Fu/W=0.3, μ=2, T0/W=0), c) linear viscoelastic isolation system (γ=0.1, Tb=2π/ωb=2 s, and ξb=0.25), and d) SCSS isolation system (γ=0.1, Tb=2π/ωb=2.0 s, and μb=0.25). In all cases, two friction coefficients were considered at the support: μk=0.1 (solid line) and 0.3 (dotted line). The complementary cumulative distribution functions (CCDF) in Figure 13 are from near-source motions (left column plots) and far-field motions (right column plots). This example illustrates that as the friction coefficient μk decreases, the probabilities of maximum block displacements become higher, which holds for both sites and the four support conditions studied. This example also shows that the frequency content of the ground motion has a significant impact on the displacement CCDFs. For instance, with the exception of the anchored blocks, it can be observed that the conditional probabilities P(D>d|PGA) are higher at the far-field site (i.e., low-frequency ground motions) than at the near-source site (i.e., high-frequency ground motions).

Similarly, Figure 14 shows cross sections of the fragility functions for the maximum block acceleration A for three fixed PGA values and increasing a values. This example considers an equipment anchored to a fixed base (Teq=0.1 s, Fu/W=0.3, μ=2, T0/W=0) and two friction coefficients: μk=0.1 (solid lines) and 0.3 (dotted lines). From Figure 14, it is apparent that the probability of exceeding an acceleration value “a” decreases with increasing friction coefficient. Likewise, Figure 14 shows that the frequency content of the ground motion has a significant effect on the maximum acceleration response.

(a)

(a)

(b)

(b)

(c)

(c)

(d)

(d)

(d)

(d)

Figure 13. Complementary cumulative distribution functions (CCDF) of the maximum block displacement at the sites SCRU (near sources, left) and CU (far-field, right) for a block simply supported (a) on a fixed base, (b) anchored to a fixed base, (c) on a viscoelastic isolation system with Tb=2s and (4) on a SCSS isolation system with Tb=2s. Two values of the base friction coefficients are considered (μk=0.1 and 0.3).

Figure 14. Complementary cumulative distribution functions (CCDF) of the maximum block acceleration of a block anchored to a fixed base derived from near-source (left) and far-field (right) ground motions.

## 3.5 damage exceedance rates

The damage exceedance rate functions λDd and λAa were computed from Equations (13) and (14), respectively, using numerical integration. A summary of the main findings is presented next.

## 3.5.1 Maximum block displacement

Figures 15 and 16 show λDd computed for simply supported, anchored, and base-isolated equipment. Additionally, seismic hazard curves (black lines) for the peak ground displacement (PGD) are also presented. Separate curves were developed for sites SCRU (near-source, NS) and CU (far-field, FF). Recall that all displacements D smaller than d0=0.01 m are regarded as ‘zero’ or ‘negligible’ displacement; therefore, the plateau of each damage rate function is the rate corresponding to ‘D=0’.

The examination of these damage rate functions helps to identify the most efficient (or inefficient) support conditions within the context of performance-based design. For example, at the near-source site SCRU (solid lines), the block displacements of freestanding equipment (Figure 15a) associated with a 1000-year return period (i.e., D1000) are 0.16, 0.10 and 0.06 m for kinetic friction coefficients of μk=0.1, 0.15 and 0.2, respectively. Anchored equipment with Fu/W=0.3 (Figure 15b) resulted in D1000=2.3 cm for μk=0.1 and D1000≤1.0 cm for higher base friction. Analogously, the 10000-year return period displacement (i.e., D10000) for freestanding equipment is almost twice that computed for the anchored equipment, mainly for friction coefficients μk>0.1. In addition, it is apparent that increasing the anchor strength decreases the displacement exceedance rates (Figure 15c) and that the prestress load on the anchors has only a marginal effect on the risk reduction (Figure 15d). For a summary of the computed D1000 and D10000 values, refer to Table B2 in Appendix B.

At the far-field site CU (dashed lines), the D1000 values for the freestanding equipment are 0.035 m for μk=0.1, and negligible otherwise. Additionally, D1000 and D10000 are negligible for all the anchored block configurations studied, making it a very effective displacement control method.

(b)

(b)

(a)

(a)

(d)

(d)

(c)

(c)

Figure 15. Risk curves for maximum block displacement at the sites SCRU (near source, solid lines) and CU (far-field, dotted lines) for equipment simply supported (a) on a fixed base, (b) anchored to a fixed base with varying friction coefficient, (c) anchored with varying FuW ratio, and (d) anchored with varying prestress load ratio T0W. The hazard curve for PGD is included as a reference.

Finally, notice that the D hazard curve of the free and anchored blocks at the far-field site CU (i.e., low-frequency ground motions) is lower than the PGD hazard curve for a wide range of return periods. At the near-source site SCRU (i.e., high-frequency ground motions), the D hazard curves are slightly higher than the PGD hazard curves for hazard levels between ~5×10-4 and ~10-5.

For blocks supported on linear viscoelastic and SCSS isolators (Figure 16), the displacement risk decreases with increasing base friction and with increasing fundamental period. This result was observed for both near-source and far-field sites. See Table B3 in Appendix B for a summary of reference D1000 and D10000 values for base-isolated equipment.

(b)

(b)

(a)

(a)

(d)

(d)

(c)

(c)

Figure 16. Risk curves for maximum block displacement at the sites SCRU (near source, solid lines) and CU (far-field, dotted lines) for equipment simply supported (a) on a viscoelastic isolation system with Tb=1 s, (b) on a viscoelastic isolation system with Tb=2 s, (c) on a SCSS isolation system with Tb=1 s, and (d) on a SCSS isolation system with Tb=2 s. Three values of the base friction coefficient are considered. The hazard curve for PGD is included as a reference.

While Figures 15 and 16 allow evaluation of how the design parameters affect λD(d) and λA(a), it is not simple to compare the relative performance between different support conditions. For this purpose, Figure 17 shows a direct comparison of the four support configurations for near-source (left) and far-field (right) sites: i) freestanding (μk=0.1), ii) anchored (μk=0.1,  Teq=0.1 s, Fu/W=0.3, μ=2 and T0/W=0), iii) linear viscoelastic isolation system (μk=0.1, γ=0.1, Tb=2π/ωb=2 s, and ξb=0.25), and iv) SCSS isolation system (μk=0.1, γ=0.1, Tb=2π/ωb=2.0 s, and μb=0.25). At the near-source site, the freestanding and base-isolated blocks have similar curves λD(d), whereas at the far-field site, the risk computed in the anchored block is persistently lower.

(b)

(b)

(a)

(a)

Figure 17. Comparison of displacement risk curves for selected blocks with different support conditions and located at the (a) near-source site and (b) far-field site. Base friction μk=0.1 in all cases. In both (a) and (b), the hazard curve for PGD is included as a reference.

In the present study, the fragility functions were derived from a standard incremental dynamic analysis (IDA), a procedure that may introduce biases in the estimation of risk measures if not done carefully. To address this problem, our preliminary results using alternative ground-motion selection techniques (e.g., the conditional scenario spectra, CSS, approach as described in Arteta and Abrahamson 2019) show that the displacement risk curves of the freestanding blocks agree very well with the IDA-based approach used herein, as shown in Figure 18.

Figure 18. Comparison of displacement risk curves for a simply supported rigid block. The IDA-based curve uses fragility functions derived from a standard incremental dynamic analysis; the CSS-based approach estimates λD by adding the rates of occurrence assigned to each ground motion selected using the CSS framework (Arteta and Abrahamson 2019).

## 3.5.2 Maximum absolute block acceleration

The rates of exceedance of the maximum block acceleration λA(a) are presented in Figure 19 for several anchored blocks located at the near-source and far-field sites. Note that the risk curve λA(a) coincides with the local seismic hazard curve for a<μkg since no slippage has taken place. Once the friction is overcome and before the anchors break, the risk curve λA(a) is higher than the seismic hazard curve. Therefore, the use of anchors may be detrimental in areas of high seismicity where acceleration-sensitive equipment is used. Additionally, notice that the risk curve λA(a) drops sharply to ‘zero’ for large a values. This occurs when the block displaces enough to mobilize the base friction and the anchors reach the fracture displacement.

From Figure 19a, it is apparent that a higher base friction is desired as it leads to lower exceedance rates of the maximum block acceleration; this improvement, however, is not very significant. To illustrate this, consider Figure 19a for a PGA equal to 0.2g, where the equipment base friction resistance is already surpassed for μk=0.1; consequently, the maximum block acceleration is increased due to the anchors action. For a PGA of the same order, but considering equipment with μk=0.2 and 0.3, sliding has not occurred yet and there is no acceleration amplification, therefore λA=λy. On the other hand, Figure 19b shows that increasing Fu/W ratios result in a right shift of the risk curve (i.e., higher risk) at the near-source site, which could be important.

Figure 19. Risk curves of the maximum block acceleration for equipment (a) anchored to a fixed base with varying friction coefficient, (b) anchored to a fixed base with varying anchor strengths. In both (a) and (b), the hazard curve for PGA is included as a reference.

## 3.5.3 Summary of key observations

Since the design strategy may vary from site to site (among other aspects), we included some key observations that could be a general guidance to practitioners.

- Based on the present results, if the equipment is sensitive to absolute acceleration, the seismic risk of equipment restrained to a fixed base (e.g., using anchors) is always higher compared to that of the other simply supported equipment or base-isolated equipment, as restrainers transmit accelerations to the block in excess of the yield acceleration (i.e., in excess of μkg).

- Conversely, it is noted that when the equipment is sensitive to displacement, the restrained equipment offers greater seismic reliability with respect to other support conditions, particularly at sites subjected to low-frequency ground motions (i.e., far-field).

- Finally, when a base isolation system is selected to control the response of equipment, a cost-benefit analysis should be performed, taking into account the relative cost of base-isolated solutions. It was noted that for the two sites studied, the isolation systems with a natural period Tb=2 s achieved a better performance than that of isolation systems with Tb=1 s. Out of the two base-isolation solutions considered, in most cases the SCSS isolation system with Tb=2 s performed better than the freestanding equipment in terms of the maximum block displacements.

The current study shows the importance of identifying the performance objective (e.g., acceleration or displacement) for each type of support condition and of using site-specific ground motions in the selection and design of the most appropriate mitigation measure.

# Conclusions

This study evaluates the reliability of rigid equipment in terms of the maximum displacement and maximum acceleration during earthquakes. Four equipment configurations were analyzed: (1) equipment simply supported on the foundation; (2) equipment restrained to a fixed base with ductile anchors; (3) equipment supported on a linear viscoelastic isolation system; and (4) equipment supported on a single concave spherical sliding (SCSS) isolation system. For each configuration, numerical fragility functions were developed using incremental dynamic analyses (IDAs).

The results show that the exceedance probability functions for maximum block displacements are very sensitive to the ground motion dataset used in the IDA (Figure 13). Indeed, for freestanding and base-isolated blocks, the low-frequency ground motions (i.e., far-field) yield higher probabilities of displacements exceedance for a given PGA value compared to those of the high-frequency ground motions (i.e., near-source). Likewise, the fragility functions for maximum block acceleration (Figure 14) are also very sensitive to the underlying ground-motion dataset, with higher probabilities of block acceleration exceedance for a given PGA value observed at the near-source site.

In terms of maximum displacements (D), the use of ductile anchors significantly improves the performance of blocks at the near-source and far-field sites. Viscous base-isolation systems with natural periods Tb of 1 s and 2 s, and SCSS isolation systems with Tb=1 s yield larger displacements (D1000, D10000) than freestanding equipment, therefor its use is not recommended. In contrast, SCSS isolation systems with a period Tb=2 s and base friction μk≥0.15 yield slightly smaller D values compared to freestanding equipment.

In terms of maximum block accelerations (A), the use of ductile anchors increases the rate of exceedance of A compared to that of freestanding blocks because the anchors transmit acceleration pulses to the block in excess μkg (i.e., the ground acceleration required to overcome friction). Since the current formulation accounts for the fracture of the anchor and the yield displacement of actual anchors is very small (e.g., 1-2 mm), the maximum block acceleration will be lower than the peak ground acceleration (PGA) if the anchors fail before the arrival of the PGA and μkg<PGA. These results contrast with those obtained by Lopez Garcia and Soong (2003b) using linear elastic anchors, who argue that in most cases, the maximum block accelerations are equal to or higher than PGA.

Finally, this study presents design displacement values for sliding block supports with different support conditions and two types of input ground motion. These results contribute to the risk assessment of more complex and multicomponent systems, and the extension of this methodology to different block types and seismic settings is straightforward.

# Acknowledgements

This research was financially supported by the Project IA100519-PAPIIT-UNAM “Propuesta de una metodología para la evaluación del riesgo de deslizamiento sísmico en equipos eléctricos debido a sismo” and the National Research Center for Integrated Natural Disaster Management CONICYT/FONDAP/15110017. Additional support was provided by Facultad de Ingeniería Civil at Universidad del Desarrollo, and FONDECYT Grant No. 1170836 “SIBER-RISK: SImulation Based Earthquake Risk and Resilience of Interdependent Systems and NetworKs”. The authors are grateful for these supports. The authors also thank the anonymous reviewers for their comments and suggestions to improve this study.

# References

Arteta, C. A., & Abrahamson, N. A. (2019). Conditional Scenario Spectra (CSS) for Hazard-Consistent Analysis of Engineering Systems. Earthquake Spectra, 35(2), 737-757.

Abrahamson, N. A., & Silva, W. J. (1997). Empirical response spectral attenuation relations for shallow crustal earthquakes. Seismological research letters, 68(1), 94-127.

Agbabian, M. S., Ginell, W. S., Masri, S. F., & Nigbor, R. L. (1991). Evaluation of-earthquake damage mitigation methods for museum objects. Studies in conservation, 36(2), 111-120.

Alhan, C., & Gavin, H. P. (2005). Reliability of base isolation for the protection of critical equipment from earthquake hazards. Engineering Structures, 27(9), 1435-1449.

Arroyo, D., Garcia, D., Ordaz, M., Mora, M. A., & Singh, S. K. (2010). Strong ground-motion relations for Mexican interplate earthquakes. Journal of Seismology, 14(4), 769-785.

ASCE/SEI 7-10 (2010). Minimum design loads for buildings and other structures (ASCE/ SEI 7-10).

Aslam, M., Scalise, D. T., & Godden, W. G. (1975). Sliding response of rigid bodies to earthquake motions: A report of an analytical and experimental study of the sliding response of rigid blocks under simultaneous horizontal and vertical earthquake accelerations. ERDA.

Aydin, K. (2006). Probabilities of initiation of response modes of rigid bodies subjected to base excitations. Structural Engineering and Mechanics, 23(5), 505-523.

Bachmann, J. A., Strand, M., Vassiliou, M. F., Broccardo, M., & Stojadinović, B. (2018). Is rocking motion predictable?. Earthquake Engineering & Structural Dynamics, 47(2), 535-552.

Bray, J. D., & Travasarou, T. (2007). Simplified procedure for estimating earthquake-induced deviatoric slope displacements. Journal of Geotechnical and Geoenvironmental Engineering, 133(4), 381-392

Bouc, R. (1971). Modele mathematique d'hysteresis. Acustica, 21, 16-25.

Butcher, J. C. (2016). Numerical methods for ordinary differential equations. John Wiley & Sons.

Candia, G., Macedo, J., Jaimes, M. A., & Magna‐Verdugo, C. (2019). A New State‐of‐the‐Art Platform for Probabilistic and Deterministic Seismic Hazard Assessment. Seismological Research Letters. Seismological Research Letters. DOI: https://doi.org/10.1785/0220190025.

Choi, B., & Tung, C. D. (2002). Estimating sliding displacement of an unanchored body subjected to earthquake excitation. Earthquake Spectra, 18(4), 601-613.

CEN Eurocode 8 (2004). Design of structures for earthquake resistance. Part 1: general rules, seismic actions and rules for buildings, European Standard EN 1998-1. Comité Européen de Normalisation.

Contento, A., & Di Egidio, A. (2014). On the use of base isolation for the protection of rigid bodies placed on a multi-storey frame under seismic excitation. Engineering Structures, 62, 1-10.

Cornell, C. A. (1968). Engineering seismic risk analysis. Bulletin of the seismological society of America, 58(5), 1583-1606.

Cornell, C. A. (1969, December). A probability-based structural code. In Journal Proceedings, 66(12), 974-985

Esteva, L. (1967, July). Criterios para la construcción de espectros para diseño sísmico. In 3er Simposio Panamericano de Estructuras, Caracas, Venezuela. (in Spanish).

Garcia, D., Singh, S. K., Herráiz, M., Pacheco, J. F., & Ordaz, M. (2004). Inslab earthquakes of central Mexico: Q, source spectra, and stress drop. Bulletin of the Seismological Society of America, 94(3), 789-802

Garcia, D., Singh, S. K., Herráiz, M., Ordaz, M., & Pacheco, J. F. (2005). Inslab earthquakes of central Mexico: peak ground-motion parameters and response spectra. Bulletin of the Seismological Society of America, 95(6), 2272-2282.

Gelagoti, F., Kourkoulis, R., Anastasopoulos, I., & Gazetas, G. (2012). Rocking isolation of low‐rise frame structures founded on isolated footings. Earthquake Engineering & Structural Dynamics, 41(7), 1177-1197.

Hutchinson, T. C., & Chaudhuri, S. R. (2006). Simplified expression for seismic fragility estimation of sliding-dominated equipment and contents. Earthquake Spectra, 22(3), 709-732.

IBC 2012 (2012) International building code. International Code Council, Country Club Hills, IL, USA; 2011.

Jaimes, M. A., Reinoso, E., & Ordaz, M. (2006). Comparison of methods to predict response spectra at instrumented sites given the magnitude and distance of an earthquake. Journal of earthquake engineering, 10(06), 887-902.

Jaimes M. A., & Reinoso, E. (2006). Comparación del comportamiento de edificios en el valle de México ante sismos de subducción y de falla normal. Revista de Ingeniería Sísmica, 75, 1-22 (in Spanish).

Jaimes, M. A., Reinoso, E., & Esteva, L. (2013). Seismic vulnerability of building contents for a given occupancy due to multiple failure modes. Journal of Earthquake Engineering, 17(5), 658-672.

Jaimes, M. A., Ramirez-Gaytán, A., & Reinoso, E. (2015). Ground-motion prediction model from intermediate-depth intraslab earthquakes at the hill and lake-bed zones of Mexico City. Journal of Earthquake Engineering, 19(8), 1260-1278.

Jaimes, M. A., Lermo, J., & Garcia‐Soto, A. D. (2016). Ground‐Motion Prediction Model from Local Earthquakes of the Mexico Basin at the Hill Zone of Mexico City. Bulletin of the Seismological Society of America, 106(6), 2532-2544.

Jaimes, M. A., & Candia, G. (2018). Toppling of rigid electric equipment during earthquakes. Engineering Structures, 168, 229-242.

Jones, N. P., & Shenton III, H. W. (1990). Generalized slide-rock response of rigid blocks during earthquakes. In Proceedings, 4th US National Conference on Earthquake Engineering, Palm Springs, California.

Kiureghian, A. D., & Neuenhofer, A. (1992). Response spectrum method for multi‐support seismic excitations. Earthquake Engineering & Structural Dynamics, 21(8), 713-740.

Konstantinidis, D., & Makris, N. (2010). Experimental and analytical studies on the response of 1/4-scale models of freestanding laboratory equipment subjected to strong earthquake shaking. Bulletin of Earthquake Engineering, 8(6), 1457-1477.

Konstantinidis, D., & Nikfar, F. (2015). Seismic response of sliding equipment and contents in base‐isolated buildings subjected to broadband ground motions. Earthquake Engineering & Structural Dynamics, 44(6), 865-887.

Lin, S. L., MacRae, G. A., Dhakal, R. P., & Yeow, T. Z. (2015). Building contents sliding demands in elastically responding structures. Engineering Structures, 86, 182-191.

Lopez Garcia, D., & Soong, T. T. (2003a). Sliding fragility of block‐type non‐structural components. Part 1: unrestrained components. Earthquake Engineering & Structural Dynamics, 32(1), 111-129.

Lopez Garcia, D., & Soong, T. T. (2003b). Sliding fragility of block‐type non‐structural components. Part 2: Restrained components. Earthquake Engineering & Structural Dynamics, 32(1), 131-149.

Makris, N., & Chang, S. P. (2000). Effect of viscous, viscoplastic and friction damping on the response of seismic isolated structures. Earthquake engineering & structural dynamics, 29(1), 85-107.

Makris, N., & Black, C. J. (2002). Uplifting and overturning of equipment anchored to a base foundation. Earthquake spectra, 18(4), 631-661.

McGuire, R. K. (2008). Probabilistic seismic hazard analysis: Early history. Earthquake Engineering & Structural Dynamics, 37(3), 329-338.

Mokha, A., Constantinou, M. C., & Reinhorn, A. M. (1988). Teflon bearings in aseismic base isolation: experimental studies and mathematical modeling (No. NCEER-88/0038 TECHNICAL). Buffalo, NY: National Center for earthquake engineering research.

Newmark, N. M. (1965). Effects of earthquakes on dams and embankments. Geotechnique, 15(2), 139-160.

NTCS-2017, 2017. Normas técnicas complementarias para diseño por sismo, Reglamento de Construcciones para el Distrito Federal, Gaceta Oficial del Departamento del Distrito Federal (in Spanish).

NZS 1170.5 (2004). Standard structural design actions - Part 5 earthquake actions, Wellington, New Zealand.

Ordaz, M., & Krishna Singh, S. (1992). Source spectra and spectral attenuation of seismic waves from Mexican earthquakes, and evidence of amplification in the hill zone of Mexico City. Bulletin of the Seismological Society of America, 82(1), 24-43.

Ordaz, M., & Reyes, C. (1999). Earthquake hazard in Mexico City: Observations versus computations. Bulletin of the Seismological Society of America, 89(5), 1379-1383.

PEMEX Petróleos Mexicanos (2017). URL: http://www.pemex.com/en/press_room/ press_releases/Paginas/2017-087-national.aspx. Acceded on December 1st, 2017

Rathje, E. M., Abrahamson, N. A., & Bray, J. D. (1998). Simplified frequency content estimates of earthquake ground motions. Journal of Geotechnical and Geoenvironmental Engineering, 124(2), 150-159.

Shao, Y., & Tung, C. C. (1999). Seismic response of unanchored bodies. Earthquake Spectra, 15(3), 523-536.

Shenton III, H. W., & Jones, N. P. (1991a). Base excitation of rigid bodies. I: Formulation. Journal of Engineering Mechanics, 117(10), 2286-2306.

Shenton III, H. W., & Jones, N. P. (1991b). Base excitation of rigid bodies. II: Periodic slide-rock response. Journal of Engineering Mechanics, 117(10), 2307-2328.

Shenton III, H. W. (1996). Criteria for initiation of slide, rock, and slide-rock rigid-body modes. Journal of Engineering Mechanics, 122(7), 690-693.

Soong, T. T., Yao, G. C., & Lin, C. C. (2000). Near-fault seismic vulnerability of nonstructural components and retrofit strategies. Earthquake Engineering and Engineering Seismology, 2(2), 67-76.

Taniguchi, T. (2002). Non‐linear response analyses of rectangular rigid bodies subjected to horizontal and vertical ground motion. Earthquake engineering & structural dynamics, 31(8), 1481-1500.

Vamvatsikos, D., & Cornell, C. A. (2002). Incremental dynamic analysis. Earthquake Engineering & Structural Dynamics, 31(3), 491-514.

Vassiliou, M. F., & Makris, N. (2012). Analysis of the rocking response of rigid blocks standing free on a seismically isolated base. Earthquake Engineering & Structural Dynamics, 41(2), 177-196.

Watson-Lamprey, J., & Abrahamson, N. (2006). Selection of ground motion time series and limits on scaling. Soil Dynamics and Earthquake Engineering, 26(5), 477-482.

Wen, Y. K. (1976). Method for random vibration of hysteretic systems. Journal of the Engineering Mechanics Division, 102(2), 249-263.

APPENDIX A. Derivation of the equations of motion for a rigid block restrained with prestressed elasto-plastic-brittle (PEPB) anchors

The equation of motion of a rigid block of mass m, anchored to a fixed base and subjected to horizontal ground acceleration xg (Figure A1) can be written as

| mx+xg+μk⋅sgnxmg+FY+FX=0 | (A1) |
| --- | --- |

where mx+xg is the total block acceleration in the X direction, μk is the coefficient of kinetic friction, and g is the acceleration of gravity. The terms FX and FY are the added horizontal and vertical forces, respectively, exerted by the anchors on the block, which are a function of the block displacement x. The derivation of the forces FX and FY, presented next, take into account the large displacements and an idealized elasto-plastic-brittle model for each anchor.

Figure A1. Position of the rigid block restrained to a fixed base to the foundation in sliding motion.

From Figure A1, the deformation in the left anchor v and the right anchor w as a function of the block displacement are

| v=x0+x2+y02+z02-L0 | (A2) |
| --- | --- |
| w=x0-x2+y02+z02-L0 | (A3) |

where L0=x02+y02+z02 is the initial anchor length, (x0,y0,z0) are the anchor offsets, and the anchor deformation rates v and w are expressed in terms of the block position x and velocity x as

| v=x0+xx0+x2+y02+z02x | (A4) |
| --- | --- |
| w=-x0-xx0-x2+y02+z02x | (A5) |

As an example, Figure A2(a) shows the anchor deformations for x0=y0=z0=0.2 m as the block displacement x increases monotonically from 0 to 0.5 m. Notice that for x values greater than 50% x0, the anchor deformations v and w depart from the linear approximation ±x(x0/L0) used by Lopez Garcia and Soong (2003b). The anchors were modeled using a prestressed elasto-plastic-brittle (PEPB) element (see full derivation in Subsection 2.1.2.) with stiffness K=1030 kN, strength Fu=34.1 kN in tension and compression, ductility ratio μ=2.0, and prestress load T0=17.06 kN, i.e., 50% of the ultimate strength. At each time step, the left anchor load Fv and the right anchor load Fw are computed as

| Fv=fNLt,v,v,zv | (A6) |
| --- | --- |
| Fw =fNLt,w,w,zw | (A7) |

where zv and zw are the anchor memory parameters, and the function fNL⋅ represents the nonlinear constitutive relation. For this loading path, the forces Fv and Fw are shown in Figure A2(b); notice that for displacements less than 0.05 m, the loads match the small displacement formulation (i.e., fv,w=T0±K x (x0/L0) defined in Lopez Garcia and Soong (2003b). At large displacements, the anchors exhibit plastic behavior and both rupture in tension.

To evaluate the terms FX and FY of Equation A1, we decomposed the anchor loads into their horizontal and vertical components. Using basic trigonometry, the horizontal component of the left and right anchors are

| Fvx=Fv⋅x0+xx0+x2+y02+z02, Fwx=Fw⋅x0-xx0-x2+y02+z02 | (A8) |
| --- | --- |

from which the net horizontal force is (Figure A2(c))

| FX=2Fvx-2Fwx=2Fv⋅x0+xx0+x2+y02+z02-2Fw⋅x0-xx0-x2+y02+z02 | (A9) |
| --- | --- |

(b)

(b)

(a)

(a)

(d)

(d)

(c)

(c)

Figure A2. (a) Anchor deformations, and (b) anchor loads for a block that displaces horizontally from 0 to 0.5 m, (c) projection of anchor loads in the x-direction, and (d) projection of anchor loads in the y-direction.

Interestingly, for x≪x0 and assuming a linear elastic anchor within this range, the first-order approximation of the lateral stiffness is

| klat=dFXdx=4K0x0L02+4T0L01-x0L02 | (A10) |
| --- | --- |

which coincides with the approximation of klat by Lopez Garcia and Soong (2003b) for the case of no prestress in the anchors. For cases where T0≠0, the term 4T0L01-x0L02 must be considered for a correct assessment of the horizontal block stiffness.

Analogously, the vertical components of the left and right anchors are written as

| Fvy=Fv⋅z0x0+x2+y02+z02, Fwy=Fw⋅z0x0-x2+y02+z02 | (A11) |
| --- | --- |

and the net vertical force is given by (Figure A2(d))

| FY=2Fvy+2Fwy=2Fv⋅z0x0+x2+y02+z02+2Fw⋅z0x0-x2+y02+z02 | (A12) |
| --- | --- |

Figures A2(c) and (d) show the complex relation between the block deformation and the net loads imposed by the anchor. From Figure A2(c), it is apparent that the small displacement approximation (i.e., stiffness from Equation A10) is valid up to yielding of the anchor in tension. Once the left anchor breaks, the vertical projection of forces FY abruptly changes direction and ‘pushes the block up’ since the right anchor is still in compression.

# appendix B

Table B1 Seismic events used in this study

| No. | Date yyyy-mm-dd | Mechanism* | Mw | Hypocenter location |  |  | Number of ground motions |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  | Lat (°) | Lon (°) | Depth (km) | Near-Source |
| 1 | 1985-09-19** | S | 8 | 18.14 | -102.71 | 17 | 4 |
| 2 | 1985-09-21 | S | 7.6 | 17.62 | -101.82 | 22 | 4 |
| 3 | 1989-04-25 | S | 6.9 | 16.61 | -99.43 | 16 | 3 |
| 4 | 1996-07-15 | S | 6.6 | 17.33 | -101.21 | 27 | 3 |
| 5 | 1997-01-11 | ID-I | 7.1 | 18.34 | -102.58 | 40 | 1 |
| 6 | 1999-09-30 | ID-I | 7.4 | 16.03 | -96.96 | 47 | 6 |
| 7 | 2007-04-13 | ID-I | 6 | 17.09 | -100.44 | 41 | 2 |
| 8 | 2012-03-20 | S | 7.4 | 16.25 | -98.52 | 16 | 1 |
| 9 | 2013-08-21 | S | 6.2 | 16.79 | -99.56 | 20 | 1 |
| 10 | 2014-04-18 | S | 7.3 | 17.38 | -101.06 | 16 | 3 |
| 11 | 2017-09-07 | ID-I | 8.2 | 14.85 | -94.11 | 58 | 3 |
| 12 | 2017-09-19** | ID-I | 7.1 | 18.40 | -98.72 | 57 | 1 |

* S = Subduction interface; ID-I = Intermediate-Depth Intraslab. ** The symbol “**” denotes records used as seed in station CU (i.e., far-field)

Table B2. D1000 and D10000 (cm) values computed for freestanding and anchored blocks

| Site Location | Freestanding |  |  | Anchored (Fu/W=0.3, μ=2) |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  | μk | D1000 | D10000 | μk | D1000 | D10000 |
| Near Source | 0.10 | 16 | 45 | 0.10 | 2.3 | 36 |
|  | 0.15 | 10 | 38 | 0.15 | ≤ 1 | 17 |
|  | 0.20 | 6.0 | 30 | 0.20 | ≤ 1 | 11 |
| Far-Field | 0.10 | 3.5 | 39 | 0.10 | ≤ 1 | ≤ 1 |
|  | 0.15 | ≤ 1 | 13 | 0.15 | ≤ 1 | ≤ 1 |
|  | 0.20 | ≤ 1 | 3.4 | 0.20 | ≤ 1 | ≤ 1 |
| Site Location | Anchored block (μk=0.1, μ=2) |  |  | Anchored block (μk=0.1, μ=2) |  |  |
|  | Fu/W | D1000 | D10000 | To/W | D1000 | D10000 |
| Near Source | 0.20 | 7.9 | 49 | 0.05 | 8.4 | 46 |
|  | 0.30 | 2.4 | 36 | 0.10 | 8.7 | 47 |
|  | 0.40 | ≤ 1 | 19 | 0.15 | 9.6 | 47 |
| Far-Field | 0.20 | ≤ 1 | ≤ 1 | 0.05 | ≤ 1 | ≤ 1 |
|  | 0.30 | ≤ 1 | ≤ 1 | 0.10 | ≤ 1 | ≤ 1 |
|  | 0.40 | ≤ 1 | ≤ 1 | 0.15 | ≤ 1 | ≤ 1 |

Table B3. D1000 and D10000 (cm) values computed for viscous and SCSS isolated blocks

| Site Location | Viscous (Tb=1 s, ξb=0.25) |  |  | Viscous (Tb=2 s, ξb=0.25) |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  | μk | D1000 | D10000 | μk | D1000 | D10000 |
| Near Source | 0.10 | 29 | 70 | 0.10 | 19 | 81 |
|  | 0.15 | 20 | 63 | 0.15 | 6.8 | 56 |
|  | 0.20 | 12 | 53 | 0.20 | ≤ 1 | 31 |
| Far-Field | 0.10 | 17 | 84 | 0.10 | 17 | 91 |
|  | 0.15 | 5.0 | 52 | 0.15 | 3.1 | 55 |
|  | 0.20 | ≤ 1 | 29 | 0.20 | ≤ 1 | 29 |
| Site Location | SCSS (Tb=1 s, μy=0.25mm) |  |  | SCSS (Tb=2 s, μy=0.25mm) |  |  |
|  | μk | D1000 | D10000 | μk | D1000 | D10000 |
| Near Source | 0.10 | 21 | 72 | 0.10 | 12 | 57 |
|  | 0.15 | 13 | 74 | 0.15 | 1.5 | 36 |
|  | 0.20 | 7.7 | 65 | 0.20 | ≤ 1 | 22 |
| Far-Field | 0.10 | 3.2 | 38 | 0.10 | 2.9 | 31 |
|  | 0.15 | ≤ 1 | 19 | 0.15 | ≤ 1 | 5.8 |
|  | 0.20 | ≤ 1 | 9.3 | 0.20 | ≤ 1 | ≤ 1 |

a) Instituto de Ingeniería, UNAM, Coordinación de Ingeniería Estructural, Av. Universidad, No. 3000, CP 04510, Del. Coyoacán, México D.F. E-mail: mjaimest@iingen.unam.mx

b) Universidad del Desarrollo, Facultad de Ingeniería Civil. Av. Plaza 680 Las Condes, Santiago – Chile. National Research Center for Integrated Natural Disaster Management CONICYT/FONDAP/15110017.